## Rev. History
1839_FAT_01
Process/Freeze Panel Loop/FAT Procedure
Rev # | Description of Change | Author | WP # | Date
1 | Published | DMS Admin | NA | System
1.1 | Streamlined loop startups and required Cimplicity setup before post-insulation for process circuits | J. Armas | NA | 2015-11-19
2 | Published | DMS Admin | NA | System
2.1 | Duplicated freeze loop startup, replaced with process loop startup changes from last rev | J. Armas | NA | 2016-01-11
3 | Published | DMS Admin | NA | System
3.1 | Added process loop reaching set point to loop startup, and removed setpoint programming from post-insulation (done at pre) | J. Armas | NA | 2016-02-02
4 | Published | DMS Admin | NA | System
4.1 | Full review and update of document by team. Adding RTD resistance chart for reference. Re-certify on all procedures. | J. Armas | NA | 2016-02-22
5 | Published | DMS Admin | NA | System
5.1 | Red line update multiple sections | P. Christenson | NA | 2016-04-04
5.2 | Updated footers and rev histories | J. Armas | NA | 2016-04-05
5.3 | Updated all documents for RTD and amperage testing section |  | NA | 2016-04-28
6 | Published | DMS Admin | NA | System
6.1 | re worded line # 3 | R. Brown | NA | 2018-12-10
7 | Published | DMS Admin | NA | System
7.1 | Updated Cover Sheet to Current Version Combined multiple Excel Files into One Excel Doc | C. Picard/J. Armas | NA | 2019-03-29
8 | Published | DMS Admin | NA | System
8.1 | Updated settings selection in Freeze Panel tab to include setting set point to 41 for both 1603E and 6040. Also include HS setting for 1603E and DIF.p to 0.1 | P. Christenson | NA | 2020-02-21
9 | Published | DMS Admin | NA | System

## Process Panel FAT
| Preparation | Complete
1 | Note: The Heat Trace Commissioning Process is available for contractors on the SIPP website | N/A
2 | This FAT begins after circuit startup has been completed per the standard startup procedure
3 | Verify Cimplicity graphics/push buttons are not in future prior to starting Electrical FAT (No purple on the PLC tab)
4 | Electrical contractor or Intel electrician to provide test heat tape (250W minimum).
5 | Intel Electrical to provide test RTD (100 Ω)
| Process Panel FAT | Complete
6 | Validate Arc Flash Label is installed
7 | De-energize panel
8 | Perform a visual check for loose wires or relays inside cabinet
9 | Verify schematics for panel are located within the panel.
10 | Is the EEW cover in place? (If not, STJ and contact requestor) | Yes No
11 | What is the Arc Flash Level? | 0 1 2 3 4
12 | What is the Arc Flash Boundary?
13 | Set up barricades to the distance of the greater of the Limited Approach Boundary and Arc Flash Boundary
14 | One electrician should be logged on Cimplicity and one electrician shall remain at heat trace panel.
| Ground Fault Test | Complete
15 | Verify that the GF Test button located under Utilities in Cimplicity initiates a GF test
16 | (*) Verify on Cimplicity ground fault animations correspond to loop in panel changing state
17 | Ensure dip switches on ground fault sensing modules are in the following positions: Up/Down/Up/Down Up/Up/Up/Up
18 | Verify that the test button on each ground fault device in the panel initiates a GF test (hold for ~5 sec)
19 | (*) Verify panel initiates ground fault test for both even and odd circuits
20 | Connect minimum 30mA 120v load to load side of loop contactor on the non-SSR controlled phase to ground for an ODD loop circuit (verify using schematic in panel). NOTE: This will test ground fault sensing device
21 | Close breaker and activate all loops
22 | Ground fault sensing device should initiate ground fault test and isolate that loop.
23 | Verify Cimplicity shows a ground fault alarm for loop tested
24 | Move 120v load device to non-SSR controlled phase on an EVEN loop
25 | Close breaker and activate all loops
26 | Ground fault sensing device should initiate ground fault test and isolate that loop.
27 | Verify Cimplicity shows a ground fault alarm
28 | Disconnect single phase load
| Heat sink failure alarm | Complete
29 | Power down panel
30 | De-term wire ID 72 from PLC AC Input Card slot 5, Input 2
31 | Re-energize panel
32 | Confirm heat sink alarm in Cimplicity (heat sink alarm should latch)
33 | Attempt to reset alarm (should not clear)
34 | Power down panel, re-term wire, re-energize panel
35 | Confirm normal panel status in Cimplicity (20-30sec PLC reboot)
| Test each loop for functionality and alarms. For each loop: | Complete
36 | Record Global parameters, found on main screen top left
37 | Select ON for global parameters on each loop and confirm each loop's settings are auto-populated correctly
38 | Turn "off" global parameters on all loops
39 | Connect RTD leads to a loop (tape to the RTD to heat trace)
40 | Confirm process variable (PV) temperature (any value other than 1562°F) read at FMS
41 | Install heat trace tape to load side of contactor, connect shield to ground.
42 | Turn breaker on
43 | Activate loop through FMS screen and verify that the contactor closes.
44 | Measure amp on load side of contactor and leave meter on for monitoring
45 | Verify amp reading on loop screen, requires selecting ground fault test from utilities screen to update amp value on loop screen
46 | Trigger the low amp alarm by changing the setpoint to a value greater than the amp reading and initiate a GF test.
47 | Return the low amp setpoint to a value below the amp reading and initiate a GF test. Verify that the alarm clears.
48 | Through FMS, change set point PID to manual and turn output percentage to 50% and verify amp readings. Then change to 100%. Confirm change in amp readings for each output using clamp-on ammeter on load side of contactor.
49 | Set PID value to RTD fault setting (25%).
50 | Confirm SCR output light is flashing green. (100% SCR output light is steady green light)
51 | Change low alarm SP value to a value 15° higher than the PV temperature reading to create a low temperature alarm. Confirm Cimplicity animation changes to indicate alarm condition. Confirm local panel touch-screen indicates alarm condition (if applicable).
52 | Change low alarm SP value back to Global value. (NOTE: If alarm condition still exists, temporarily change the low alarm setpoint to a value 15° lower than the PV temperature reading. Confirm alarm stays latched on Cimplicity screen and local panel touch-screen (if applicable).
53 | Reset latched alarm and confirm alarm condition clears on Cimplicity screen and local panel touch-screen (if applicable). Change low alarm SP value back to Global value if changed to clear alarm.
54 | Change high alarm SP value to a value 15° lower than the PV temperature reading to create a high temperature alarm. Confirm Cimplicity animation changes to indicate alarm condition. Confirm local panel touch-screen indicates alarm condition (if applicable).
55 | Change high alarm setpoint value back to Global value. (NOTE: If alarm condition still exists, temporarily change the high alarm SP to a value 15° higher than the PV temperature reading. Confirm alarm stays latched on Cimplicity screen and local panel touch-screen (if applicable).
56 | Reset latched alarm and confirm alarm condition clears on Cimplicity screen and local panel touch-screen (if applicable). Change high alarm SP value back to Global value if changed to clear alarm.
57 | Change PID output to 100% Confirm SCR output light is green steady.
58 | To test circuit RTD failure: Determ a wire from RTD. The SCR will go to the RTD FAULT % OUTPUT (25%). Temperature PV will go out of control (1500+). Confirm amp output of contactor changes to value recorded earlier. Temperature and RTD Fault alarms will be generated. NOTE: PID Output % will still show 100 but PLC will reduce to 25%
59 | Reconnect RTD and confirm temperature and RTD Fault alarms will not clear until reset. Once reset PID Output will go to 100% again. Noted by SCR steady green light
60 | Connect RTD and heat tape to next loop to be tested. Repeat Steps in this section until ALL loops in panel have been tested.
Final Steps
61 | Place ALL PID Loops back in AUTO.
62 | Verify ALL breakers are OFF and ALL loops IN-ACTIVE.
63 | Create WO to FMS: Electrical process panel FAT complete, please take the panel heat sink and communications alarm out of future. Assign panel paging to electrical resource.

## Freeze Panel FAT
| Freeze Panel FAT | Complete
1 | Note: The Heat Trace Commissioning Process is available for contractors on the SIPP website | N/A
2 | This FAT begins after circuit startup has been completed per the standard startup procedure
3 | Verify cimplicity page is built before FAT (STJ if not)
4 | Verify the following items have been bullet proofed (protected) from accidental activation/strike
5 | Display Panels
6 | Power switches and buttons as necessary.
7 | Verify panel schematic is present in panel.
8 | Perform a visual check for loose wires or relays inside cabinet
9 | Verify internal EEW cover in place
10 | Verify the FMS point is landed and reference panel drawing for correct terminal points. NOTE: These points are different for Chromalox and Nelson panel types
11 | Close disconnect and open cabinet by gently defeating disconnect with paper clip/screwdriver. Note: Alarm light will flash. Put HOA switch in hand to clear alarm
12 | Verify the RTD is reading an accurate value per outside air temp
13 | Program Chromalox 1603E controller comes from Vendor Pre-programmed with below settings: Verify setpoint is 41deg F P1 = 4(deg C), 12(deg F)
14 | P2 = 0 (ENG UNITS DEG C OR DEG F AS SELECTED)
15 | P3 = 999 (ENG UNITS DEG C OR DEG F AS SELECTED)
16 | P4 = REV
17 | P5 = 4 (Alarm 1 output – Instrument failure alarm)
18 | OPERATION PARAMETER:
18 | PB = 0
19 | HS = Select FUN button 3 times, set to 0.1
20 | Program Chromalox 6040 controller with below settings: Verify setpoint is 41deg F (Main screen press far right 'Func' button until SP is displayed) Steps for entering Setup, Config an OPR. Press and hold far right 'Func' button then press down arrow key. This enters menu. Use arrow keys to toggle to Setup, Config or OPTR. Unlock code is Setup -10, Config - 20, OPR none)
20 | Setup = DIF.p 0.1
20 | Setup = Pb_P 0.0
20 | Config = input PTF (ENG UNITS DEG C OR DEG F AS SELECTED) (Unlock code for Config is 20)
20 | ruL = 999 (ENG UNITS DEG C OR DEG F AS SELECTED)
20 | rLL = 0
20 | CtrL = rev
20 | USE2 = Or_r
20 | With HOA switch set to Auto confirm contactor pulls in. Note: Setpoint may need modification based on outside temperature. If outside tempearture is above 40°F, change setpoint to a value higher than outside temperature.
20 | To change setpoint on 1603 controller, press enter key, arrow key to change temp, and press enter key again
20 | To change setpoint on 6040 controller, press FUNC key until SP is displayed, arrow key to change temp, and press FUNC key again
20 | Verify freeze protection heat trace alarms at display on the panel.
20 | Verify no circuits are landed. NOTE: If circuits are landed either de-term or contact contractor to determine if loops can be energized for testing
20 | Close all circuit breakers
20 | Press and hold (5 seconds) ‘initialize’ button
20 | Depress "Lamp Test" and verify all closed breakers are displayed.
20 | Trip circuit breakers individually. Verify panel display shows correct circuit alarm and alarm is generated in Cimplicity. Reset each breaker and confirm both local and PLC alarms clear before moving on to next circuit.
20 | Switch HOA Sw to OFF, confirm 24V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Switch HOA Sw to HAND,confirm 24V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Switch HOA Sw to AUTO, confirm 0V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Power panel off via disconnect, confirm 24V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Re-energize panel. Confirm 0V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Pull the red RTD cable in TB1 to test ambient temperature sensor fail.
20 | Confirm FMS alarm: 24V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Confirm local panel controller shows sensor fail:
20 | 6040 controller shows "open"
20 | 1603 controller shows 1500
20 | Re-terminate RTD cable on TB1. Confirm 0V on TB1 points #3 and #4 or confirm cimplicity animation
20 | Turn OFF all breakers, then press and hold (5 seconds) 'initialize' button
20 | Return controller setpoint to 40°F:
20 | Adjust setpoint to 40F on 6040 controller, press FUNC key until SP is displayed, arrow key to change temp, and press FUNC key again
20 | Adjust setpoint to 40F on 1603 controller, press enter key, arrow key to change temp, and press enter key again
20 | Verify cabinet heater is set at 50°F or 10°C if applicable
20 | Submits workorder to FMS to remove panel from FUTURE and enable alarming to electrical resource

## Process Loop Startup
Step | Pre Insulation FAT | Complete
1 | NOTE: Requestor will arrange for loop owner to be present at time requested (through eRequest)
2 | Create a startup package (Start-up checklist, ECR, Panel Schedule and e-Request) for the circuit(s) being requested. Save a copy of the Start-up Checklist in the pre-insulation folder for that building.
3 | Confirm panel schedule installed and correct. NOTE: If load name is not correct pre-insulation will need to be rejected until name can be updated. Contractor will bger responsible for updating. Walk can be completed but contractor cannot be released for insulation until panel schedule updated.
4 | Inspect heat trace end to end.
5 | Confirm all splice boxes, end of line boxes, etc. are accessible (6 ft above catwalks, 8 ft from ground). Heat trace not ran on piping must be in flexible conduit Note: Stainless steel tags should also be installed at this point
6 | If all is correct release contractor for insulation. Approval indicated by completed erequest, if any issues, decline request with comments. Add any issues to startup checklist comments.
7 | Instruct the Loop Owner the following is their responsibility to complete via eRequest to FMS or Physically go to PUB1 2nd fl E/6 BEFORE the post-insulation request can be completed: -Take the loop out of future, or no paging will work -Verify/Change PV, high/low alarm setpoints as needed -Setup the paging group alarm will page to, and the alarm message as needed - Failure will delay any Post Insulation requests.
Step | Post Insulation
1 | NOTE: Requestor must arrange for loop owner to be present at time requested.
2 | Retrieve the ECR (or startup checklist)* for the circuit(s) requested from the pre-insulation folder that resides within the ECR folder for the building being worked in. *Startup checklist is not required to be saved if ECR is available.
3 | Ensure circuit has been removed from the future class in Cimplicity and the description matches EZP.
4 | Confirm process variable temperature reading is any value other than 1562°F on Cimplicity screen and local panel touch screen as applicable.
5 | Startup loop per startup checklist. Note:All labels are required to be stainless tags for exterior
6 | Check continuity phase-phase and phase-ground on load side of loop contatctor. NOTE: Phase to Phase reading will show continuity
7 | Place clamp-on ammeter on load side of contactor for loop to be tested.
8 | Energize circuit to be tested.
9 | Place loop in manual and set percentage to 100%.
10 | Activate loops one at a time (noting inrush current), then wait at least 10 minutes after each loop activation to confirm the correct loop heats up. This confirms proper wiring of heat tape and RTD.
11 | Place loop at 50% output
12 | Walk line from end to end, confirm end of line lights are all working, they will be blinking at this point.
13 | Place loop into Auto and confirm all setpoints are correct and reset any alarms, global setpoint off, ground fault bypass off. Validate Temp RTD limit 5 sec, RTD fault 25%, low current 0. NOTE: If any temperature alarms exist due to FAT, alarm may not be able to be cleared until loop stabilizes.
14 | Allow the PV to increase to SP, after loop reaches set point, verify SSR output reduces to 0%. Note: If this does not occur within 15 minutes, STOP the FAT process and reject the eRequest with comments to the requestor loop will not maintian temperature
15 | Electrical FAT is now complete with system owner

## Freeze Loop Startup
Step | Pre Insulation | Complete
1 | NOTE: Requestor will arrange for loop owner to be present at time requested (through eRequest). If no SO present we do not do the walk.
2 | Create a startup package for the circuit(s) being requested; startup checklist, ECR, panel schedule, and erequest. Save a copy of the ECR/startup checklist in the pre-insulation folder for the building. *Startup checklist is not required to be saved if ECR is available.
3 | Confirm panel schedule installed and correct. NOTE: If load name is not correct pre-insulation will need to be rejected until name can be updated. Contractor responsible for getting load name updated. Walk can be completed but contractor cannot be released for insulation until panel schedule updated.
4 | Instruments shall be wrapped for 21W (number of wraps depends on size of tape).
5 | Inspect heat trace end to end with SO.
6 | Confirm all splice boxes, end of line boxes, etc. are accessible (6 ft above catwalks, 8 ft from ground). Heat Trace must be run in flexible conduit when not installed pipe. NOTE: Stainless tags need to be installed at this point,
7 | If all is correct release contractor for insulation. Approval indicated by completed erequest, if any issues, decline request with comments. Add any issues to startup checklist comments.
Step | Post Insulation | Complete
8 | Retrieve the startup checklist for the circuit(s) requested from the pre-insulation folder that resides within the ECR folder for the building being worked in. Print out the rest of the startup package, panel schedule, ECR, and erequest.
9 | Log-in to Cimplicity and verify panel is active, shelve panel alarms to be tested for appropriate time for startup.
10 | Assess panel ARC Flash label for PPE requirements
11 | Shock hazard PPE must be worn for non EEW panels.
12 | Startup freeze loop per startup checklist
14 | Inspect heat trace end to end with SO. Note: If no SO present we do not do the walk. SO is responsible for ensuring their high point vents, low point drains, and instrumentation is appropriately heat traced per their system design or P&ID
15 | Record heat tape wattage and length on startup checklist. (To use as reference for later step)
16 | Confirm all splice boxes, end of line boxes, etc. are accessible (6 ft above catwalks, 8 ft from ground). Confirm stainless tags are correct. If circuit branches, each branch must have an end of line light. Flexible conduit must be sealed when entering PVC jacket of insulation and oriented on bottom to prevent leaks in insulation
17 | Record ambient temperature off of panel Controller, to be documented on Freeze Panel PM Amp Log on EasyPower Drive
18 | Place clamp-on ammeter on load side of terminal block for circuit to be tested
19 | Place panel in HAND in order to pull in contactor
20 | Energize circuits to be tested one at a time with ammeter in place prior to energizing circuit to ensure a proper max amp reading is recorded.
21 | Record max startup inrush amps (Record on Freeze Panel PM Amp Log)
22 | Confirm all end-of-line lights illuminate when energized
23 | After 15 minutes record steady-state amps (Record on Freeze Panel PM Amp Log) Note: Use [(Length*Wattage)/208v] to get rough approx of steady state amperage value. NOTE: This is a rough value
24 | Press and hold (5 seconds) ‘initialize’ button (if applicable)
25 | Press ‘Display Test’ to confirm associated LEDs correctly illuminate for new circuits (if applicable)
26 | Trip GFCI breaker for circuits to be tested
27 | For each tripped circuit confirm FMS animation changes to alarm state by either Viewing Cimplicity or reading 24v at TB1
28 | For each tripped circuit confirm correct circuit alarm on panel display (if applicable)
29 | Reset all circuit breakers that were tripped for testing
30 | Place panel in AUTO
31 | Update Freeze Panel PM Amp Log
32 | Submit FMS request to activate Freeze Loop and alarming